## Electrical QC Checklist
Applicable | Incorporated | Confirmed | Electrical QC Checklist
|  |  | Project # | 25999999 | EXAMPLE PROJECT NAME | 2025-10-20 | Filters
|  |  | Topic | Category | Item | Notes | Standard | Healthcare | Sports | Site Plan | Food Service / Kitchen | Demolition / Renovation | Utility Service Entrance | Duct Bank (Feeder or Utility Service Entrance) | ATS | Exterior Generator or Fuel Tank | Indoor Generator Room | Exterior Lighting | Helipad | Elevator / Escalator | Fire Pump | Fire Command Center | Emergency Radio Communication System | Fire Alarm | FILTERING
FALSE | FALSE | FALSE | General | Specifications | All applicable specification sections included |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | General | Specifications | Specifications are edited for project specific scope |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | General | Specifications | Specifications identify applicable codes including energy code(s) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | General | Specifications | Specifications for conductors (copper, aluminum, or both) are consistent with schedules and owner direction |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | General | Renovation | Construction sequence / phasing is considered and temporary electrical equipment or requirements are identified. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | General | Renovation | Existing to remain, existing to be removed, new work is clearly identified |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | General | Renovation | Standard ICRA notes are included for healthcare projects |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | General | Renovation | Demolition plans clearly identify equipment/scope as “existing to remain” or “existing to be removed” |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | General | Renovation | Equipment to be turned over to Owner is defined |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | General | Environmental | Requirements for bracing and certification are designated based on building location, use, seismic category and importance factor |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | General | Environmental | For hurricane zones, design wind speeds for risk category III and IV building are designated for exterior lighting, helipad lighting , and PV systems |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | General | Environmental | For high ambient temperature areas, capacity of generators and/or exterior transformers has been derated |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | General | Environmental | For high altitude areas, capacity of generators and/or exterior transformers has been derated |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | General | Environmental | For corrosive environments, equipment construction is specified appropriately |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Feeder Schedule | Standard feeder schedule is used. Use of aluminum, if shown, matches specification requirements |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Transformer Schedule | Standard transformer schedule is used. Use of aluminum conductors and/or windings, if shown, matches specification requirements |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | ATS Schedule | Standard Automatic Transfer Switch schedule is used and completed |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Schedules | ATS Schedule | Available fault current fields are completed |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Schedules | ATS Schedule | Priority levels with time delays are assigned |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Schedules | Equipment Connection Schedules | Mechanical equipment connection schedule is complete |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Equipment Connection Schedules | Elevator/escalator connection schedule is complete |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Schedules | Equipment Connection Schedules | Vendor Equipment connection schedule is complete |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Equipment Connection Schedules | Food service connection schedules are complete |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Schedules | Equipment Connection Schedules | Lab equipment connection schedule is complete |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedule provided for each panelboard and distribution panel on distribution diagram |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedules are complete |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedule includes calculated available fault current value and required AIC rating |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedule indicates MCB vs. MLO requirements |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Calculated demand load + spare capacity is less than the panel rating and 80% of upstream OCP |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | For transformer applications, upstream feeder breaker and downstream main breaker sizing matches transformer schedule |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedule indicates required spares and spaces (recommend 20% spare capacity and breaker mounting space) Verify owner specific requirements. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedule enclosure configuration matches proposed location (i.e. surface vs. flush, hazardous, NEMA 1, 3, 4X, etc.) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedule includes 3 pole breaker for connection to SPD. Schedule denotes internal versus external mounting. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedule includes notes for ARMS reduction approach for 1200A and higher breaker sizes per NEC 240.87 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Schedule type reflects required construction and configuration (i.e. panelboard, distribution panel, MCC, switchboard, isolation) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Multi section or riser configured panels reflect feed-thru or sub feed lug configuration |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Where schedule includes more than 42 poles, schedule notes define tub configuration (single vs. double) and space is allocated accordingly |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Shunt trip breakers scheduled for elevators and kitchen equipment beneath hoods (Schedule extra pole for panelboard construction) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Where GFCI is indicated clarify 5mA or 30 mA based on intended purpose. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Life Safety/Emergency panels serve permitted loads only |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Isolated ground bus indicated, where needed |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Where substantially oversized feeders are used, annotation for oversized lugs included on schedule. This may require a different type of equipment if oversized lugs cannot accommodate. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | Specialized panel types are identified (i.e. fusible coordination panel, branch circuit level metering panel, etc.) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Panel Schedules | For breakers larger than 20A, wire size is indicated or branch circuit conductor schedule is included (applies to connections not already addressed in a connection schedule) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Equipment Naming Convention Detail | Naming Convention edited for project scope (i.e. number of levels/areas) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Equipment Naming Convention Detail | Naming Convention coordinated with existing equipment for renovations/additions |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Lighting Fixture Schedule | Standard fixture schedule is used, when practical |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Lighting Fixture Schedule | Standard fixture naming convention is used |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Lighting Fixture Schedule | Project specific fixtures follow same format as standard schedule with associated fields completed |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Lighting Fixture Schedule | Fixture selections match associated control requirements |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Lighting Fixture Schedule | Fixture voltage selection matches circuiting on lighting plans |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Lighting Fixture Schedule | Mounting height for suspended and wall bracket fixtures is indicated (on schedule or floor plans) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Lighting Fixture Schedule | Fixture selection is suitable for specialty areas (MRI, Corrosion Resistant, Cleanroom, food service, hazardous, etc.) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Schedules | Lighting Fixture Schedule | Fixture wattage is indicated with appropriate units (i.e. w/fixture or w/linear foot) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Utility/Customer Owned Service Coordination | Electric Company service drop location terminal point, metering is identified |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Utility/Customer Owned Service Coordination | Utility underground or overhead easement coordinated with civil, where required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Utility/Customer Owned Service Coordination | Transformer/switchgear pad location is accessible to utility trucks |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Utility/Customer Owned Service Coordination | Utility requirements for pad and location are indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Utility/Customer Owned Service Coordination | Equipment protection bollards provided (coordinate with civil/utility standards) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Utility/Customer Owned Service Coordination | Transformer/switchgear placement complies with insuring agency guidelines ( i.e. Factory Mutual Data Sheet 5-4) and utility guidelines |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Utility/Customer Owned Service Coordination | Low Voltage System conduit routing indicated (unless shown by other disciplines) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Duct Banks | Conduit runs coordinated with other utilities (water, sewer, gas, telecom, storm, etc.) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Duct Banks | Conduit runs coordinated with structural (i.e. grade beams, footings, foundation walls, etc.) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Duct Banks | Manholes and/or pullboxes shown, where needed, for long runs and for change in direction |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Duct Banks | Spare conduits provided (under drives, service entrance, stubbed out from electrical room, etc.) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Duct Banks | Minimum and/or maximum cover detail for conduits. Identify where concrete cover, steel plate or encasement is required. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Duct Banks | Derating considered based on depth and soil conditions |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Duct Banks | Bend radii considered for large duct bank runs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Pole base details provided. Use appropriate wind speed schedule in the detail (see "Pole Base" Electrical Design Guide) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Appropriate lighting level in parking areas and driveways (perform calculations) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Fixture selections meet IES BUG rating requirements for project application (Backlight, Uplight, Glare) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Where required by LEED or local codes, lighting meets cutoff restrictions at property line |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Lighting power densities meet tradeable and non-tradeable allotments per energy code (ASHRAE 90.1 or IECC) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Stair lighting is provided at exterior stairs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Generator, mechanical yard, transformer yards are illuminated adequately (provide emergency/life safety inside generator enclosure, or at generator locations) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Landscape lighting/sign lighting/flagpole lighting provided, if applicable |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Exit discharge lighting is indicated to right-of-way or as required by AHJ |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Façade lighting is provided, where applicable |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Entrance/Canopy areas are properly illuminated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Site entrance and building signage powered and controlled |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Obstruction lights, if needed (if not shown on roof plan) current FAA Advisory Circular 70/7460-IL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Lighting | Lighting control sequence is clearly identified for each fixture type (may be defined on control matrix instead) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | Location and orientation indicated, space allotted for sound attenuation, where needed |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | Coordinate with Landscape plans to ensure trees are not near exhaust discharge |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | Sufficient space allowed for generator ventilation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | Provide power for generator accessory loads if not equipped with load center in enclosure |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | Fuel tank is accessible to refueling trucks (within standard hose length) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | Remote refueling port where generator main fuel tank is not readily accessible |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | Generator connection box (for roll-up generator and/or load bank connection) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | Specified fuel tank (UL 142 versus UL 2085) is appropriate based upon separation from property line and/or combustibles (see "Generator" Electrical Design Guide) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Generator | EPO Switch location is shown |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Equipment placement takes into consideration flood plane historical data |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Screen walls coordinated with Civil engineer/architect |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Snow melting areas indicated where requested by owner |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power provided for irrigation system equipment |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power and/or rough-in for Security Cameras indicated if in project scope. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power for heat trace/freeze protection (i.e. cooling tower condenser water lines) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Weatherproof GFCI convenience outlets shown . Ensure receptacles within 25' of air conditioning equipment (NEC 210.63) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power for seasonal lighting. Provide controlled circuits if requested. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power for Electric Vehicle (EV) charging stations provided or roughed-in for future |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power at O2 park provided |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power and lighting for Ambulance parking area, if located onsite |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power for emergency phone/blue light stations |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power for parking control equipment and/or security barriers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power and lighting for water features, pond aerators |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Security call boxes, card readers, keypads, access gates (power and signal) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Helipad - Approach paths are shown, with FATO and TLOF lighting, Heliport beacon, and illuminated wind sock |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Outdoor mechanical and plumbing equipment indicated including any hot box connections |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Plumbing/Civil lift stations, de-watering systems, etc. are indicated |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power for portable equipment (mobile technology trucks, tent/exhibition, tour busses, mass casualty laydown area, etc.) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power for Loading dock equipment (levelers, lifts, lights) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Power for Compactors and bailer equipment |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Site Plan | Other Considerations | Post Indicator Valve (PIV) location indicated with fire alarm supervision |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Room is properly rated (see "Electrical Rooms" Electrical Design Guide) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Rooms are stacking, where possible, and not located beneath wet spaces (restrooms, food service, etc.) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Rooms are placed to allow for conduit access in/out of room (i.e. avoid pinning between elevators, stairs and exterior wall) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Rooms with transformers are located away from sound/vibration sensitive areas |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Door quantity and placement comply with NEC requirements |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Doors swing outward with panic hardware where required (Rooms where equipment is rated 800A or more per NEC 110.26(C)(3); Request doors to swing outward even when not code required) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Room arrangement allows for removal/replacement of largest equipment component in the room - (verify door heights, ceiling heights, elevator weight limits, etc. needed to get equipment clear from the building) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Proper working clearance is provided on equipment room plans per NEC 110.26, 110.31 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Rear access provided for large equipment, where required |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Allow 84" deep front aisle space where using portable lifter and transfer truck for draw out breakers - standard clearance is insufficient |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Dedicated equipment space is maintained above electrical equipment - clear of ductwork/piping/dampers per NEC 110.26(E) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Layout accommodates different vendor equipment offerings |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Equipment layout minimizes transformer secondary conductor lengths in accordance with NEC 240.21(C)(2) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Arrangement allows for expansion of switchboards/switchgear and indicates reserved mounting space for future sections |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Space reserved for lighting control cabinets, spare fuse cabinet, portable lifting device storage, battery system equipment, remote operator panels, fire extinguishers |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Space reserved for externally mounted SPDs adjacent to associated equipment |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Arrangement allows for space separation/mechanical protection between emergency and normal equipment/feeders |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Space reserved for conduit risers/sleeves and/or block outs for connection to spaces above/below. Ensure coordination with Structural Engineer and beam locations |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Cooling/ventilation requirements coordinated with Mechanical. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Transformers are floor mounted where possible (not beneath panels). Limit suspended transformers to 75 kVA or smaller. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Where transformers are stacked, confirm total rack/transformer height is coordinated with ceiling/structural height |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Transformers placed to allow clearances on sides and in back to allow for ventilation |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Convenience outlets are provided |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Equipment pads are coordinated |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | UPS room - coordinate ventilation requirements for battery storage racks (some ventilation required even for VRLA batteries) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | UPS room – may need to calculate volume of electrolyte in required number of batteries to determine proper room rating per IBC 509.7, if applicable |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Electrical Rooms | Electrical rooms: All or part of lighting connected to Critical or Emergency circuit at ATS locations for Life Safety/Emergency |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Generator room is 2 hour rated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Where code allows, man door to generator room should swing inward to allow egress when room pressure goes negative |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | EPO switch location is shown |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Selected receptacles connected to life safety or emergency panel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Battery charger power connection is indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Day tank location shown (for Diesel Generators) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Power connections shown for engine block heater and other generator accessories |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Intake air damper operators connected to priority 1 power source and coordinated to open asap with engine start |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Where possible, limit fuel storage in building to 660 gal/tank with a total aggregate of 1320 gal. Fuel storage capacity complies with room rating and NFPA 37-6.3 (3 hour if more than 5000 gallons in generator room) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Where room or skid fuel tanks are provided (not connected to underground tanks) pathway with man door provided for access for refueling purposes |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Coordinate with mechanical for provision of heat in generator room for cold weather environments to prevent pipes from freezing |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Battery powered emergency lights provided on Life Safety/Emergency circuit per NFPA 110-7.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Generator Rooms | Heat detectors indicated (in lieu of smoke detection) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Stairwells: Minimum light levels provided (10 fc) as recommended by IES. (some local codes may mandate minimum levels.) Stair sections provided, where needed, to convey lighting at intermediate landings. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Stairwells: Power and control for smoke control/pressurization equipment denoted to be routed within 2-HR stair or chase or provided with 2-HR rated cable assembly or suitable fire barrier per IBC 909.20.6 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Power shown to sump pump and/or pit GFI receptacle. High water alarm connected to separate circuit from sump pump. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Elevator equipment room is 2 hour rated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Nothing passes through the elevator equipment room that is not associated with elevator service |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | GFI receptacles dedicated to equipment room are provided |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Disconnect for power unit on strike side of door is provided |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Disconnect for cab lights on strike side of door is provided (Life Safety or Emergency Power) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Smoke and heat detectors indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Lighting in elevator equipment room provides a minimum of 19 fc at the floor per ASME A17.1-2.7.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Elevator Pits: Enclosed fixtures provided to provide 10 fc on floor, with switch provided at access ladder per ASME A17.1-2.2.5.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Life safety/emergency lighting is shown near elevator thresholds to provide adequate illumination (5 fc required for threshold inside cab - recommend same for threshold on lobby side) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Where elevators are required for fire service, associated equipment room HVAC should also connect to Equipment/Required standby power, lighting is provided at each level within the shaft |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Escalator Pits: Enclosed circuit breaker provided in upper pit (usually, but confirm with architect). Small work light (10 fc) and receptacle provided in upper and lower pits (can connect to common circuit and run within escalator skirt) Do not shunt trip power. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Escalators evenly illuminated with a minimum of 5 fc per ASME A17.1-6.1.7.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Trash Chutes/Linen Chutes: Provide power connection for door safety interlock system |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Vertical Transportation | Power and disconnect shown for wheelchair lifts |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Disconnect/VFD/Controller locations shown on electrical plans (referenced to mechanical plans) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Plenum lights/switches shown for field fabricated plenums and power connection tag shown for unit mounted lights/switches |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Power provided for control panels |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Power for filter units, if required |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | VFD's placed to limit motor circuit length to 150' (to avoid additional measures to mitigate reflected wave) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Chiller room: EPO for Chiller power per IMC 1106.5.1. Verify accomplished via BMS or provide electrical means |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Chiller room: power for refrigerant air monitoring alarm panel |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Boiler room: EPO for boiler power if state adopts ASME CSD-1, or IMC 1006.8. Verify accomplished via BMS or provide electrical means. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Boiler room, gas water heater room: CO monitoring - connect to fire alarm or verify connected to BMS |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Boiler room, gas water heater room: Heat detectors indicated (in lieu of smoke detection) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Mechanical Rooms | Chiller room refrigerant purge fans connected to required standby or equipment branch (or monitored for IIAR standard if connected to normal power) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | Communication room power is consistent with Design Guide |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | Provision of communications backboards and rack locations is coordinated with systems specifications/designer and clearly defined |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | Provision of communications cable tray is coordinated with systems specifications/designer and clearly defined |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | Provision of communications grounding is coordinated with systems specifications/designer and clearly defined |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | Shunt trip breakers and EPO pushbutton shown for rooms where required per NEC 645 where UPS systems are provided |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | Lighting connected to Critical circuit for healthcare applications, Emergency for non-healthcare applications where life safety communications systems are contained in space. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | Critical power circuit shown for nurse call terminal cabinet for healthcare applications |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | Circuits provided for A/V equipment, security, access control, etc. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | NEMA configuration for rack mounted UPS equipment indicated where required connected to. Critical for healthcare applications. Emergency for emergency radio communication system equipment, or Optional Standby for remaining. Normal power circuits (if standby is not available) is coordinated with owner. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Equipment Rooms | Communications Rooms | At least one critical power convenience receptacle on dedicated circuit provided for healthcare applications |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | All equipment (Switchgear, switchboards, distribution panel, panelboards, ATS's, UPS's, etc.) are identified in accordance with naming convention schedule |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Bus sizes, breaker sizes, indicated for switchboards and switchgear (for which schedules are not provided). For MV breakers, CT ratios are indicated and trip functions are indicated |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | For main-tie-main switchboards and switchgear, tie breaker matches the main breaker/bus size in frame size and trip unit (trip setting of tie reduced to allow for better coordination) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Feeder sizing corresponds to scheduled upstream OCP and downstream panel rating |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Feeder sizes adjusted to compensate for voltage drop, where required to meet 2% limitation per energy code(s) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | ATS pole configuration is coordinated with generator grounding approach (i.e. where generator neutral is grounded, provide 3pole/4 pole switches; where generator neutral is ungrounded, provide 3 pole/3 pole SN switches) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Generator sizing accounts for de-rating factors for high ambient temperature, high elevation, nonlinear loads, fuel source deviations | If either is selected (Exterior OR Interior Generator Room) on this one | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Surge protection devices are indicated for preliminary issue packages until panel schedules are included in issue package (identify whether internally or externally mounted, coordinate with spec) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Transformer sizes are indicated |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Special transformer configurations are indicated (i.e. proper K rating indicated, phase shifting, etc.) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Customer metering points are indicated, and specifications included regarding interface with BAS. Method for isolation of loads by type for metering purposes is clear (panel level, circuit level, etc.) Identify all submeters which may be required for load summary and/or tenant loads. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Utility metering is indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Where protective devices with relays are required, desired functions to be programmed are clearly defined |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Ground fault protection is properly indicated for normal service (i.e. two levels for healthcare); per NEC 230 and 215. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Conductor quantity is correctly indicated (i.e. 'N' subscript for three wire circuits, 'G' subscript for service entrance) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Circuits requiring 2 hour protection are identified (i.e. emergency feeders NEC 700.10 routed above ceilings, fire pump feeders NEC 695.6, circuits serving stair pressurization fans, generator control wiring (i.e. AIS to generator) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Fire pump service configuration is code compliant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Fire pump controller to motor connection is properly sized/identified (i.e. 6 conductors at 58% for wye-delta starter configuration) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Breaker de-rating indicated, if needed (i.e. insulated case breakers with X/R rating greater than 6.6) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Rule-of-thumb sizing criteria used to enable selective coordination (i.e. for 0.1 second - 4:1 molded case breakers, 2:1 fuses). Published breaker/breaker and breaker/fuse tables used for selective coordination of all currents/all times (for non-healthcare, 2014 NEC and later) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Normal power and emergency power sequence of operation is defined. Include demand response and/or peak load limiting/reduction as applicable to project requirements. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Distribution Diagrams and Risers | Power Distribution Diagrams | Arc Flash Reduction is indicated on required breakers (size 1200A and above per NEC 240.87) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Lighting plans are complete |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Lighting calculations are complete for representative areas, indicating design illuminance per IESNA standard. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Life safety/emergency lighting is shown (including small assembly spaces, elevator thresholds) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Exit signage shown and consistent with life safety egress plans (including small assembly spaces) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Exit signage placement is consistent ceiling conditions (i.e. avoids full height door swings, soffit height allow required minimum of 7`-0`` clearance, pendant mounting scheduled where needed, etc.) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Exit discharge lighting is shown and connected to Life Safety or emergency circuits (if not on site plan) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Along entire egress path, no space is left with a single fixture/source creating a single point of failure |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Lighting power density is within limits defined for associated energy code compliance path |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Daylight harvesting zones are indicated where required |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Appropriate lighting is provided in shell spaces |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Circuit calculations are based on maximum fixture wattage |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Lighting control is defined for each space or space type, and is consistent with energy code requirements |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Lighting Plans | General | Under cabinet and/or display lighting is controlled separately from general illumination in the space |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Power plans are complete |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Electrical equipment locations are identified, either on floor plans or enlarged scale plans |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Connections for various types of equipment have been included. Refer to Design Guide for sample list |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Areas requiring switching of receptacles per energy code are identified. |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Annunciator panels are located for Generator, Fire alarm, elevator status, ATS status. Power circuit provided where applicable |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | General purpose receptacle provided in corridors within 25' from end of corridor and 50' max on center |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Cable tray routing and sizing is indicated |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Note is provided prohibiting conduit routing in elevated slabs (See also NEC 518.4 for specific restrictions for assembly occupancies) |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Weatherproof GFI outlets shown within 25' of roof mounted heating, air conditioning and refrigeration equipment |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Locations of building expansion joints are clearly evident in architectural backgrounds and instructions in specs or details provided for conduit routing across joints |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Receptacle mounting heights and device types are as requested by owner |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Power Plans | General | Power operated doors with push plates shown |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Operating Room | Isolation panels are provided and placed to minimize branch circuit length and associated leakage currents |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Operating Room | Equipment and outlets likely to come into contact with patient are connected to isolation panel (i.e. does not need to include boom lights) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Operating Room | X-ray and Laser outlets are labeled and have NEMA configuration identified |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Operating Room | Ceiling mounted locking receptacle, cord and plug, retractable reel provided, where needed |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Operating Room | 24 hour clock, interval timer, and reset button provided, if not shown on technology plans |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Recovery Room | Heating equipment is connected to critical power circuit |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Patient Room | Room lighting and shading is controllable from patient bed as required by LEED or owner direction. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Patient Room | Headwall area is served by minimum of 2 branch circuits, one of which is normal power and one is critical branch |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Patient Room | Normal circuits at headwall originate from same panel (except special equipment) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Patient Room | Tamper resistant devices shown for pediatric and psychiatric patient rooms |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Tub Room | GFCI receptacle shown for hoist equipment |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Nurse Station | Location of control point for corridor lighting control. (Dual level or dimming preferred for nighttime lighting reduction) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Nurse Station | Task lighting provided and switched separately from general lighting |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Nurse Station | General lighting connected to Critical Branch |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Nurse Station | Receptacles are connected to critical power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Nurse Station | Med Gas alarm panel is provided with Life Safety circuit |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Nurse Station | Blood Bank refrigerator and alarm are connected to critical power (separate circuits) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Medication | Power provided for Narcotic locker power "open" indication light/alarm system |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Medication | Power connection for medicine refrigerator connected to critical power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Medication | Power connection provided for cabinet security |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | ICU/CCU | Fixture selected to minimize glare |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Laboratory | Local switch provided for disconnect of 'hard-wired' equipment. Note for provision of label for each switch |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Laboratory | Multiple circuits are provided to allow for circuit separation of sensitive equipment |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Laboratory | Selected equipment and processors provided with critical power circuit |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Laboratory | Processor equipment connected to UPS where possible, or via isolation transformer |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | Radiology: 'X-Ray In Use' sign above entrance door and interlocked with room lighting control |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | Radiology: nonferrous construction fixtures with no UV, IR, or RF emissions used for MRI suites |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | Conductors to be provided by contractor are clearly identified (size and quantity) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | Disconnecting means to be provided by contractor is identified |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | Note provided referencing vendor drawings used as basis of design |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | RFI filters provided for MRI rooms |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | Conduits entering Linear Accelerator room at 45 degree or greater relative to iso-center |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | X-ray room lead shield fits behind any flush mounted devices shown in space |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | Isolated ground power is provided for CT Scan equipment if required by vendor |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Healthcare Space Specific Requirements | Radiology | Conductors are sized to comply with vendor voltage drop limitations and minimum conductor sizing |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Fire Alarm Control Panel indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Fire Alarm Voice Evacuation system indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Fire Fighter's Smoke Control Panel indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Area of Rescue assistance, stairwell/elevator lobby communication system base station indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Generator remote annunciator indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Automatic transfer switch control and/or status panel, where provided indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Fire pump remote annunciator, if not integral to fire alarm control panel indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Elevator status remote annunciator indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Security monitors indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Access Control System controls/ stairwell lock overrides indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Master Medical Gas remote alarm panel (two panels) indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Blood Bank remote alarm indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Narcotics security alarm indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Documentation cabinet for fire alarm system documentation indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | 24 Hour Station/Fire Command Room | Method/Space allotted for storage of building design documents |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Kitchen/Food Service/Vending Areas | GFCI devices shown where accessible, or remote protection (breaker or remote trip/reset device) where inaccessible |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Kitchen/Food Service/Vending Areas | Lighting control allows for safe operation of equipment |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Kitchen/Food Service/Vending Areas | Shunt trip breakers indicated for food service equipment beneath hood |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Kitchen/Food Service/Vending Areas | Where required, fixtures are gasketed to prevent grease/insect infiltration |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Kitchen/Food Service/Vending Areas | In high circuit concentration areas, panelboards are located, flush mounted, within associated space. Provide stainless steel enclosure where required by AHJ. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Catwalk | Catwalk configuration allows for proper working clearance for electrical equipment |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Catwalk | Spotlight power connections ((1) L15-30R and (1) 5-20R) are indicated for each spotlight platform |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Catwalk | Photostrobe power connections are indicated (minimum 24-20A/1 circuits for arenas, 30-30A/1 circuits for stadiums. Circuits route through contactor with remote 'off' switch located per owner direction. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Catwalk | Dimmed or multi-level switched circulation lighting, controlled by lighting control system, is provided at catwalk -part on Emergency circuit |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Catwalk | Acceptance from AHJ received for placement of emergency panelboards on catwalk where seating bowl is not sprinklered |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Catwalk | Company switch or disconnects provided for added power on catwalk for use by owner as needed |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Catwalk | Power provided for house reduction curtain rigging systems |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Training Room | One GFI receptacle located at each treatment/taping table |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Training Room | Power indicated for cryotherapy chamber, if required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Training Room | Power indicated for bariatric chamber, if required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Training Room | Power indicated for ice machines |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Training Room | Power indicated for Hydrocollator equipment |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Press Seating | Provide minimum 1 duplex for each 2 seats along press seating counter. May require wiremold along counter with pigtail connection to receptacles at the ends of each row. Detail is provided where needed. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Hydrotherapy | Note is included requiring contractor to provide bonding in accordance with NEC 680 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Interview Room | Theatrical bars or recessed theatrical fixtures for stage illumination. Separate dimming controller for stage fixtures |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Dressing Rooms | Switches provided for receptacles at dressing counter with indicating light outside space per NEC 520.73 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Dressing Rooms | Switches provided for lighting at dressing counter, separate from general illumination |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Space Specific | Home Team Locker Rooms | Receptacle is provided in lockable portion of each player locker unit |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | General | Fire alarm control, DACT and NAC panels locations are indicated and life safety/emergency power provided and matches equipment indicated on Fire Alarm riser, if provided |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | General | Consideration of anticipated average ambient sound levels (NFPA 72-A.18.4.4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | General | Acoustically distinguishable spaces are noted, special consideration made for intelligibility are denoted (i.e. large lobbies with hard surfaces) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | General | Notification zones are indicated on floor plans, where other than single zone for the building |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | General | Where multiple notification zones are provided, circuit survivability requirements (NFPA 72-23.10.2, -24.3.13) are indicated and documented for submission to AHJ. (For most projects, level 2 or 3 construction will be required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | General | Note provided referring to mechanical and fire protection drawings for quantities and locations of duct smoke detectors, flow and tamper switches |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Floor plans are complete |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Proper notification appliance symbols are shown (i.e. speaker vs. horn) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Smoke detectors are shown in vicinity of any panels containing control functions (NFPA 72-10.4.4). Provide detector whether or not panel is located in an attended location. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Device layout accounts for sound pressure losses for finishes and through barriers (i.e. 40-45 dBA drop through 4" partition, 12-20 dBA drop through closed hollow core door, 20-30 dBA drop through closed solid core door, 2 dBA drop for acoustic tile ceiling, 3 dBA drop for carpeting) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Visible notification appliances are not installed in exit stairs (due to increase in trip hazard) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Visible Devices are shown in required public mode spaces: restrooms, conference rooms, training rooms, waiting rooms, lobbies, lounges, etc. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Where mechanical design includes engineered smoke control zones, the sprinkler zoning and fire alarm zoning matches the smoke zoning |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Visible notification appliances are placed within 15' of the end of corridors |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Where required by code, smoke detectors are provided within 10' of the entrance to stair tower at each level for activation of stairwell smoke pressurization system. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Manual pull stations are located within 5' from exit doorways at each level, and on both sides of grouped openings over 40' wide. Intermediate pull stations located for travel distances over 200'. (NFPA 72-17.14.8., 101-9.6.2, IBC 907.6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | At least one pull station is provided near FACP for facilities for which manual pull stations are omitted and only automatic initiation means are provided (i.e. arenas) (NFPA 101-9.6.2.6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Smoke detectors are located more than 26" horizontal path from door to a bathroom containing a shower or tub (unless detector is listed for the application) (NFPA 101-9.6.2.10.5, IBC 907.2.11.4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Smoke detectors are not located within 10' of fixed cooking equipment (unless listed for installation). Detectors installed between 10' and 20' from fixed cooking equipment shall have alarm silencing means or be photoelectric type.(NFPA 101-9.6.2.10.4, IBC 907.2.11.3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Voice system is specified for High rise, assembly occupancies over 1000 occupants, educational, and mercantile occupancies) (IBC 907.2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | First responder radio system/DAS is connected to Life Safety/Emergency power and generator and/or battery system allows for an operating duration of not less than 24 hours. (IBC 2702.2.3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Approval received from AHJ if Pre-Signal Alarm sequence is specified (NFPA 101, NFPA 72-23.8.1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Approval received from AHJ if Positive Alarm sequence is specified (NFPA 101, NFPA 72-23.8.1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Detectors required for elevator recall and shutdown are shown in lobbies, shaft and equipment room |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Floor Plan Specific Items (Where Floor Plans are Provided in Construction Documents) | Low frequency sounder base detectors and high candela strobes are shown in public mode notification area sleeping rooms/on-call rooms |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Fire Alarm Riser | Anticipated control panels, NAC panels and remote annunciators are indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Fire Alarm Riser | Wiring configuration (Class A vs. Class B) corresponds to specifications |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Fire Alarm Riser | Areas where circuit survivability are required are indicated with the survivability level |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Fire Alarm Riser | Return path for Class A communications loop is identified, where applicable |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Fire Alarm System | Fire Alarm Riser | Sequence of operation is included and edited for project specific requirements |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Systems | Emergency Radio Communication System | Provisions are included in base bid for Bi-Directional Antenna system riser cable routing, roof access, control panel and annunciator panel mounting. Specifications include complete system installation as a bid alternate (for owner purchase if coverage is determined to be needed based on as built audio survey once structure and skin are constructed). |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Systems | Emergency Radio Communication System | 2-HR room and riser pathway for system are included in documents |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Systems | Emergency Radio Communication System | Power circuit provided |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Systems | Emergency Radio Communication System | Proposed annunciator location is indicated |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
FALSE | FALSE | FALSE | Other Systems | Emergency Radio Communication System | System schematic is provided |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE
Refresh

## Project Information
Project Information
Project Name: | EXAMPLE PROJECT NAME
Project Number: | 25999999
Date: | 2025-10-20
Project Filters Select ALL That Are Applicable
Standard | TRUE
Healthcare | FALSE
Sports | FALSE
Site Plan | FALSE
Food Service / Kitchen | FALSE
Demolition / Renovation | FALSE
Utility Service Entrance | FALSE
Duct Bank (Feeder or Utility Service Entrance) | FALSE
ATS | FALSE
Exterior Generator or Fuel Tank | FALSE
Indoor Generator Room | FALSE
Exterior Lighting | FALSE
Helipad | FALSE
Elevator / Escalator | FALSE
Fire Pump | FALSE
Fire Command Center | FALSE
Emergency Radio Communication System | FALSE
Fire Alarm | FALSE

## Filters (EPIC) (hidden)
Filters
| Standard | Healthcare | Sports | Site Plan | Food Service / Kitchen | Demolition / Renovation | Utility Service Entrance | Duct Bank (Feeder or Utility Service Entrance) | ATS | Exterior Generator or Fuel Tank | Indoor Generator Room | Exterior Lighting | Helipad | Elevator / Escalator | Fire Pump | Fire Command Center | Emergency Radio Communication System | Fire Alarm
All applicable specification sections included | 1
Specifications are edited for project specific scope | 1
Specifications identify applicable codes including energy code(s) | 1
Specifications for conductors (copper, aluminum, or both) are consistent with schedules and owner direction | 1
Construction sequence / phasing is considered and temporary electrical equipment or requirements are identified. | [5 empty] | 1
Existing to remain, existing to be removed, new work is clearly identified | [5 empty] | 1
Standard ICRA notes are included for healthcare projects |  | 1
Demolition plans clearly identify equipment/scope as “existing to remain” or “existing to be removed” | [5 empty] | 1
Equipment to be turned over to Owner is defined | [5 empty] | 1
Requirements for bracing and certification are designated based on building location, use, seismic category and importance factor | 1
For hurricane zones, design wind speeds for risk category III and IV building are designated for exterior lighting, helipad lighting , and PV systems | 1
For high ambient temperature areas, capacity of generators and/or exterior transformers has been derated | 1
For high altitude areas, capacity of generators and/or exterior transformers has been derated | 1
For corrosive environments, equipment construction is specified appropriately | 1
Standard feeder schedule is used. Use of aluminum, if shown, matches specification requirements | 1
Standard transformer schedule is used. Use of aluminum conductors and/or windings, if shown, matches specification requirements | 1
Standard Automatic Transfer Switch schedule is used and completed | [8 empty] | 1
Available fault current fields are completed | [8 empty] | 1
Priority levels with time delays are assigned | [8 empty] | 1
Mechanical equipment connection schedule is complete | 1
Elevator/escalator connection schedule is complete | [13 empty] | 1
Vendor Equipment connection schedule is complete | 1
Food service connection schedules are complete |  |  |  |  | 1
Lab equipment connection schedule is complete | 1
Schedule provided for each panelboard and distribution panel on distribution diagram | 1
Schedules are complete | 1
Schedule includes calculated available fault current value and required AIC rating | 1
Schedule indicates MCB vs. MLO requirements | 1
Calculated demand load + spare capacity is less than the panel rating and 80% of upstream OCP | 1
For transformer applications, upstream feeder breaker and downstream main breaker sizing matches transformer schedule | 1
Schedule indicates required spares and spaces (recommend 20% spare capacity and breaker mounting space) Verify owner specific requirements. | 1
Schedule enclosure configuration matches proposed location (i.e. surface vs. flush, hazardous, NEMA 1, 3, 4X, etc.) | 1
Schedule includes 3 pole breaker for connection to SPD. Schedule denotes internal versus external mounting. | 1
Schedule includes notes for ARMS reduction approach for 1200A and higher breaker sizes per NEC 240.87 | 1
Schedule type reflects required construction and configuration (i.e. panelboard, distribution panel, MCC, switchboard, isolation) | 1
Multi section or riser configured panels reflect feed-thru or sub feed lug configuration | 1
Where schedule includes more than 42 poles, schedule notes define tub configuration (single vs. double) and space is allocated accordingly | 1
Shunt trip breakers scheduled for elevators and kitchen equipment beneath hoods (Schedule extra pole for panelboard construction) | 1
Where GFCI is indicated clarify 5mA or 30 mA based on intended purpose. | 1
Life Safety/Emergency panels serve permitted loads only | 1
Isolated ground bus indicated, where needed | 1
Where substantially oversized feeders are used, annotation for oversized lugs included on schedule. This may require a different type of equipment if oversized lugs cannot accommodate. | 1
Specialized panel types are identified (i.e. fusible coordination panel, branch circuit level metering panel, etc.) | 1
For breakers larger than 20A, wire size is indicated or branch circuit conductor schedule is included (applies to connections not already addressed in a connection schedule) | 1
Naming Convention edited for project scope (i.e. number of levels/areas) | 1
Naming Convention coordinated with existing equipment for renovations/additions | 1
Standard fixture schedule is used, when practical | 1
Standard fixture naming convention is used | 1
Project specific fixtures follow same format as standard schedule with associated fields completed | 1
Fixture selections match associated control requirements | 1
Fixture voltage selection matches circuiting on lighting plans | 1
Mounting height for suspended and wall bracket fixtures is indicated (on schedule or floor plans) | 1
Fixture selection is suitable for specialty areas (MRI, Corrosion Resistant, Cleanroom, food service, hazardous, etc.) | 1
Fixture wattage is indicated with appropriate units (i.e. w/fixture or w/linear foot) | 1
Electric Company service drop location terminal point, metering is identified | [6 empty] | 1
Utility underground or overhead easement coordinated with civil, where required | [6 empty] | 1
Transformer/switchgear pad location is accessible to utility trucks | [6 empty] | 1
Utility requirements for pad and location are indicated | [6 empty] | 1
Equipment protection bollards provided (coordinate with civil/utility standards) | [6 empty] | 1
Transformer/switchgear placement complies with insuring agency guidelines ( i.e. Factory Mutual Data Sheet 5-4) and utility guidelines | [6 empty] | 1
Low Voltage System conduit routing indicated (unless shown by other disciplines) | [6 empty] | 1
Conduit runs coordinated with other utilities (water, sewer, gas, telecom, storm, etc.) | [7 empty] | 1
Conduit runs coordinated with structural (i.e. grade beams, footings, foundation walls, etc.) | [7 empty] | 1
Manholes and/or pullboxes shown, where needed, for long runs and for change in direction | [7 empty] | 1
Spare conduits provided (under drives, service entrance, stubbed out from electrical room, etc.) | [7 empty] | 1
Minimum and/or maximum cover detail for conduits. Identify where concrete cover, steel plate or encasement is required. | [7 empty] | 1
Derating considered based on depth and soil conditions | [7 empty] | 1
Bend radii considered for large duct bank runs | [7 empty] | 1
Pole base details provided. Use appropriate wind speed schedule in the detail (see "Pole Base" Electrical Design Guide) | [11 empty] | 1
Appropriate lighting level in parking areas and driveways (perform calculations) | [11 empty] | 1
Fixture selections meet IES BUG rating requirements for project application (Backlight, Uplight, Glare) | [11 empty] | 1
Where required by LEED or local codes, lighting meets cutoff restrictions at property line | [11 empty] | 1
Lighting power densities meet tradeable and non-tradeable allotments per energy code (ASHRAE 90.1 or IECC) | [11 empty] | 1
Stair lighting is provided at exterior stairs | [11 empty] | 1
Generator, mechanical yard, transformer yards are illuminated adequately (provide emergency/life safety inside generator enclosure, or at generator locations) | [11 empty] | 1
Landscape lighting/sign lighting/flagpole lighting provided, if applicable | [11 empty] | 1
Exit discharge lighting is indicated to right-of-way or as required by AHJ | [11 empty] | 1
Façade lighting is provided, where applicable | [11 empty] | 1
Entrance/Canopy areas are properly illuminated | [11 empty] | 1
Site entrance and building signage powered and controlled | [11 empty] | 1
Obstruction lights, if needed (if not shown on roof plan) current FAA Advisory Circular 70/7460-IL | [11 empty] | 1
Lighting control sequence is clearly identified for each fixture type (may be defined on control matrix instead) | [11 empty] | 1
Location and orientation indicated, space allotted for sound attenuation, where needed | [9 empty] | 1
Coordinate with Landscape plans to ensure trees are not near exhaust discharge | [9 empty] | 1
Sufficient space allowed for generator ventilation | [9 empty] | 1
Provide power for generator accessory loads if not equipped with load center in enclosure | [9 empty] | 1
Fuel tank is accessible to refueling trucks (within standard hose length) | [9 empty] | 1
Remote refueling port where generator main fuel tank is not readily accessible | [9 empty] | 1
Generator connection box (for roll-up generator and/or load bank connection) | [9 empty] | 1
Specified fuel tank (UL 142 versus UL 2085) is appropriate based upon separation from property line and/or combustibles (see "Generator" Electrical Design Guide) | [9 empty] | 1
EPO Switch location is shown | [9 empty] | 1
Equipment placement takes into consideration flood plane historical data |  |  |  | 1
Screen walls coordinated with Civil engineer/architect |  |  |  | 1
Snow melting areas indicated where requested by owner |  |  |  | 1
Power provided for irrigation system equipment |  |  |  | 1
Power and/or rough-in for Security Cameras indicated if in project scope. |  |  |  | 1
Power for heat trace/freeze protection (i.e. cooling tower condenser water lines) | 1
Weatherproof GFCI convenience outlets shown . Ensure receptacles within 25' of air conditioning equipment (NEC 210.63) | 1
Power for seasonal lighting. Provide controlled circuits if requested. | 1
Power for Electric Vehicle (EV) charging stations provided or roughed-in for future |  |  |  | 1
Power at O2 park provided |  | 1
Power and lighting for Ambulance parking area, if located onsite |  | 1
Power for emergency phone/blue light stations |  |  |  | 1
Power for parking control equipment and/or security barriers |  |  |  | 1
Power and lighting for water features, pond aerators |  |  |  | 1
Security call boxes, card readers, keypads, access gates (power and signal) |  |  |  | 1
Helipad - Approach paths are shown, with FATO and TLOF lighting, Heliport beacon, and illuminated wind sock | [12 empty] | 1
Outdoor mechanical and plumbing equipment indicated including any hot box connections | 1
Plumbing/Civil lift stations, de-watering systems, etc. are indicated | 1
Power for portable equipment (mobile technology trucks, tent/exhibition, tour busses, mass casualty laydown area, etc.) | 1
Power for Loading dock equipment (levelers, lifts, lights) | 1
Power for Compactors and bailer equipment | 1
Post Indicator Valve (PIV) location indicated with fire alarm supervision | 1
Room is properly rated (see "Electrical Rooms" Electrical Design Guide) | 1
Rooms are stacking, where possible, and not located beneath wet spaces (restrooms, food service, etc.) | 1
Rooms are placed to allow for conduit access in/out of room (i.e. avoid pinning between elevators, stairs and exterior wall) | 1
Rooms with transformers are located away from sound/vibration sensitive areas | 1
Door quantity and placement comply with NEC requirements | 1
Doors swing outward with panic hardware where required (Rooms where equipment is rated 800A or more per NEC 110.26(C)(3); Request doors to swing outward even when not code required) | 1
Room arrangement allows for removal/replacement of largest equipment component in the room - (verify door heights, ceiling heights, elevator weight limits, etc. needed to get equipment clear from the building) | 1
Proper working clearance is provided on equipment room plans per NEC 110.26, 110.31 | 1
Rear access provided for large equipment, where required | 1
Allow 84" deep front aisle space where using portable lifter and transfer truck for draw out breakers - standard clearance is insufficient | 1
Dedicated equipment space is maintained above electrical equipment - clear of ductwork/piping/dampers per NEC 110.26(E) | 1
Layout accommodates different vendor equipment offerings | 1
Equipment layout minimizes transformer secondary conductor lengths in accordance with NEC 240.21(C)(2) | 1
Arrangement allows for expansion of switchboards/switchgear and indicates reserved mounting space for future sections | 1
Space reserved for lighting control cabinets, spare fuse cabinet, portable lifting device storage, battery system equipment, remote operator panels, fire extinguishers | 1
Space reserved for externally mounted SPDs adjacent to associated equipment | 1
Arrangement allows for space separation/mechanical protection between emergency and normal equipment/feeders | 1
Space reserved for conduit risers/sleeves and/or block outs for connection to spaces above/below. Ensure coordination with Structural Engineer and beam locations | 1
Cooling/ventilation requirements coordinated with Mechanical. | 1
Transformers are floor mounted where possible (not beneath panels). Limit suspended transformers to 75 kVA or smaller. | 1
Where transformers are stacked, confirm total rack/transformer height is coordinated with ceiling/structural height | 1
Transformers placed to allow clearances on sides and in back to allow for ventilation | 1
Convenience outlets are provided | 1
Equipment pads are coordinated | 1
UPS room - coordinate ventilation requirements for battery storage racks (some ventilation required even for VRLA batteries) | 1
UPS room – may need to calculate volume of electrolyte in required number of batteries to determine proper room rating per IBC 509.7, if applicable | 1
Electrical rooms: All or part of lighting connected to Critical or Emergency circuit at ATS locations for Life Safety/Emergency | 1
Generator room is 2 hour rated | [10 empty] | 1
Where code allows, man door to generator room should swing inward to allow egress when room pressure goes negative | [10 empty] | 1
EPO switch location is shown | [10 empty] | 1
Selected receptacles connected to life safety or emergency panel | [10 empty] | 1
Battery charger power connection is indicated | [10 empty] | 1
Day tank location shown (for Diesel Generators) | [10 empty] | 1
Power connections shown for engine block heater and other generator accessories | [10 empty] | 1
Intake air damper operators connected to priority 1 power source and coordinated to open asap with engine start | [10 empty] | 1
Where possible, limit fuel storage in building to 660 gal/tank with a total aggregate of 1320 gal. Fuel storage capacity complies with room rating and NFPA 37-6.3 (3 hour if more than 5000 gallons in generator room) | [10 empty] | 1
Where room or skid fuel tanks are provided (not connected to underground tanks) pathway with man door provided for access for refueling purposes | [10 empty] | 1
Coordinate with mechanical for provision of heat in generator room for cold weather environments to prevent pipes from freezing | [10 empty] | 1
Battery powered emergency lights provided on Life Safety/Emergency circuit per NFPA 110-7.3 | [10 empty] | 1
Heat detectors indicated (in lieu of smoke detection) | [10 empty] | 1
Stairwells: Minimum light levels provided (10 fc) as recommended by IES. (some local codes may mandate minimum levels.) Stair sections provided, where needed, to convey lighting at intermediate landings. | 1
Stairwells: Power and control for smoke control/pressurization equipment denoted to be routed within 2-HR stair or chase or provided with 2-HR rated cable assembly or suitable fire barrier per IBC 909.20.6 | 1
Power shown to sump pump and/or pit GFI receptacle. High water alarm connected to separate circuit from sump pump. | [13 empty] | 1
Elevator equipment room is 2 hour rated | [13 empty] | 1
Nothing passes through the elevator equipment room that is not associated with elevator service | [13 empty] | 1
GFI receptacles dedicated to equipment room are provided | [13 empty] | 1
Disconnect for power unit on strike side of door is provided | [13 empty] | 1
Disconnect for cab lights on strike side of door is provided (Life Safety or Emergency Power) | [13 empty] | 1
Smoke and heat detectors indicated | [13 empty] | 1
Lighting in elevator equipment room provides a minimum of 19 fc at the floor per ASME A17.1-2.7.9 | [13 empty] | 1
Elevator Pits: Enclosed fixtures provided to provide 10 fc on floor, with switch provided at access ladder per ASME A17.1-2.2.5.1 | [13 empty] | 1
Life safety/emergency lighting is shown near elevator thresholds to provide adequate illumination (5 fc required for threshold inside cab - recommend same for threshold on lobby side) | [13 empty] | 1
Where elevators are required for fire service, associated equipment room HVAC should also connect to Equipment/Required standby power, lighting is provided at each level within the shaft | [13 empty] | 1
Escalator Pits: Enclosed circuit breaker provided in upper pit (usually, but confirm with architect). Small work light (10 fc) and receptacle provided in upper and lower pits (can connect to common circuit and run within escalator skirt) Do not shunt trip power. | [13 empty] | 1
Escalators evenly illuminated with a minimum of 5 fc per ASME A17.1-6.1.7.2 | [13 empty] | 1
Trash Chutes/Linen Chutes: Provide power connection for door safety interlock system | 1
Power and disconnect shown for wheelchair lifts | 1
Disconnect/VFD/Controller locations shown on electrical plans (referenced to mechanical plans) | 1
Plenum lights/switches shown for field fabricated plenums and power connection tag shown for unit mounted lights/switches | 1
Power provided for control panels | 1
Power for filter units, if required | 1
VFD's placed to limit motor circuit length to 150' (to avoid additional measures to mitigate reflected wave) | 1
Chiller room: EPO for Chiller power per IMC 1106.5.1. Verify accomplished via BMS or provide electrical means | 1
Chiller room: power for refrigerant air monitoring alarm panel | 1
Boiler room: EPO for boiler power if state adopts ASME CSD-1, or IMC 1006.8. Verify accomplished via BMS or provide electrical means. | 1
Boiler room, gas water heater room: CO monitoring - connect to fire alarm or verify connected to BMS | 1
Boiler room, gas water heater room: Heat detectors indicated (in lieu of smoke detection) | 1
Chiller room refrigerant purge fans connected to required standby or equipment branch (or monitored for IIAR standard if connected to normal power) | 1
Communication room power is consistent with Design Guide | 1
Provision of communications backboards and rack locations is coordinated with systems specifications/designer and clearly defined | 1
Provision of communications cable tray is coordinated with systems specifications/designer and clearly defined | 1
Provision of communications grounding is coordinated with systems specifications/designer and clearly defined | 1
Shunt trip breakers and EPO pushbutton shown for rooms where required per NEC 645 where UPS systems are provided | 1
Lighting connected to Critical circuit for healthcare applications, Emergency for non-healthcare applications where life safety communications systems are contained in space. | 1
Critical power circuit shown for nurse call terminal cabinet for healthcare applications |  | 1
Circuits provided for A/V equipment, security, access control, etc. | 1
NEMA configuration for rack mounted UPS equipment indicated where required connected to. Critical for healthcare applications. Emergency for emergency radio communication system equipment, or Optional Standby for remaining. Normal power circuits (if standby is not available) is coordinated with owner. | 1
At least one critical power convenience receptacle on dedicated circuit provided for healthcare applications |  | 1
All equipment (Switchgear, switchboards, distribution panel, panelboards, ATS's, UPS's, etc.) are identified in accordance with naming convention schedule | 1
Bus sizes, breaker sizes, indicated for switchboards and switchgear (for which schedules are not provided). For MV breakers, CT ratios are indicated and trip functions are indicated | 1
For main-tie-main switchboards and switchgear, tie breaker matches the main breaker/bus size in frame size and trip unit (trip setting of tie reduced to allow for better coordination) | 1
Feeder sizing corresponds to scheduled upstream OCP and downstream panel rating | 1
Feeder sizes adjusted to compensate for voltage drop, where required to meet 2% limitation per energy code(s) | 1
ATS pole configuration is coordinated with generator grounding approach (i.e. where generator neutral is grounded, provide 3pole/4 pole switches; where generator neutral is ungrounded, provide 3 pole/3 pole SN switches) | [8 empty] | 1
Generator sizing accounts for de-rating factors for high ambient temperature, high elevation, nonlinear loads, fuel source deviations | [9 empty] | 1 | 1
Surge protection devices are indicated for preliminary issue packages until panel schedules are included in issue package (identify whether internally or externally mounted, coordinate with spec) | 1
Transformer sizes are indicated | 1
Special transformer configurations are indicated (i.e. proper K rating indicated, phase shifting, etc.) | 1
Customer metering points are indicated, and specifications included regarding interface with BAS. Method for isolation of loads by type for metering purposes is clear (panel level, circuit level, etc.) Identify all submeters which may be required for load summary and/or tenant loads. | 1
Utility metering is indicated | [6 empty] | 1
Where protective devices with relays are required, desired functions to be programmed are clearly defined | 1
Ground fault protection is properly indicated for normal service (i.e. two levels for healthcare); per NEC 230 and 215. | 1
Conductor quantity is correctly indicated (i.e. 'N' subscript for three wire circuits, 'G' subscript for service entrance) | 1
Circuits requiring 2 hour protection are identified (i.e. emergency feeders NEC 700.10 routed above ceilings, fire pump feeders NEC 695.6, circuits serving stair pressurization fans, generator control wiring (i.e. AIS to generator) | 1
Fire pump service configuration is code compliant | [14 empty] | 1
Fire pump controller to motor connection is properly sized/identified (i.e. 6 conductors at 58% for wye-delta starter configuration) | [14 empty] | 1
Breaker de-rating indicated, if needed (i.e. insulated case breakers with X/R rating greater than 6.6) | 1
Rule-of-thumb sizing criteria used to enable selective coordination (i.e. for 0.1 second - 4:1 molded case breakers, 2:1 fuses). Published breaker/breaker and breaker/fuse tables used for selective coordination of all currents/all times (for non-healthcare, 2014 NEC and later) | 1
Normal power and emergency power sequence of operation is defined. Include demand response and/or peak load limiting/reduction as applicable to project requirements. | 1
Arc Flash Reduction is indicated on required breakers (size 1200A and above per NEC 240.87) | 1
Lighting plans are complete | 1
Lighting calculations are complete for representative areas, indicating design illuminance per IESNA standard. | 1
Life safety/emergency lighting is shown (including small assembly spaces, elevator thresholds) | 1
Exit signage shown and consistent with life safety egress plans (including small assembly spaces) | 1
Exit signage placement is consistent ceiling conditions (i.e. avoids full height door swings, soffit height allow required minimum of 7`-0`` clearance, pendant mounting scheduled where needed, etc.) | 1
Exit discharge lighting is shown and connected to Life Safety or emergency circuits (if not on site plan) | 1
Along entire egress path, no space is left with a single fixture/source creating a single point of failure | 1
Lighting power density is within limits defined for associated energy code compliance path | 1
Daylight harvesting zones are indicated where required | 1
Appropriate lighting is provided in shell spaces | 1
Circuit calculations are based on maximum fixture wattage | 1
Lighting control is defined for each space or space type, and is consistent with energy code requirements | 1
Under cabinet and/or display lighting is controlled separately from general illumination in the space | 1
Power plans are complete | 1
Electrical equipment locations are identified, either on floor plans or enlarged scale plans | 1
Connections for various types of equipment have been included. Refer to Design Guide for sample list | 1
Areas requiring switching of receptacles per energy code are identified. | 1
Annunciator panels are located for Generator, Fire alarm, elevator status, ATS status. Power circuit provided where applicable | 1
General purpose receptacle provided in corridors within 25' from end of corridor and 50' max on center | 1
Cable tray routing and sizing is indicated | 1
Note is provided prohibiting conduit routing in elevated slabs (See also NEC 518.4 for specific restrictions for assembly occupancies) | 1
Weatherproof GFI outlets shown within 25' of roof mounted heating, air conditioning and refrigeration equipment | 1
Locations of building expansion joints are clearly evident in architectural backgrounds and instructions in specs or details provided for conduit routing across joints | 1
Receptacle mounting heights and device types are as requested by owner | 1
Power operated doors with push plates shown | 1
Isolation panels are provided and placed to minimize branch circuit length and associated leakage currents |  | 1
Equipment and outlets likely to come into contact with patient are connected to isolation panel (i.e. does not need to include boom lights) |  | 1
X-ray and Laser outlets are labeled and have NEMA configuration identified |  | 1
Ceiling mounted locking receptacle, cord and plug, retractable reel provided, where needed |  | 1
24 hour clock, interval timer, and reset button provided, if not shown on technology plans |  | 1
Heating equipment is connected to critical power circuit |  | 1
Room lighting and shading is controllable from patient bed as required by LEED or owner direction. |  | 1
Headwall area is served by minimum of 2 branch circuits, one of which is normal power and one is critical branch |  | 1
Normal circuits at headwall originate from same panel (except special equipment) |  | 1
Tamper resistant devices shown for pediatric and psychiatric patient rooms |  | 1
GFCI receptacle shown for hoist equipment |  | 1
Location of control point for corridor lighting control. (Dual level or dimming preferred for nighttime lighting reduction) |  | 1
Task lighting provided and switched separately from general lighting |  | 1
General lighting connected to Critical Branch |  | 1
Receptacles are connected to critical power |  | 1
Med Gas alarm panel is provided with Life Safety circuit |  | 1
Blood Bank refrigerator and alarm are connected to critical power (separate circuits) |  | 1
Power provided for Narcotic locker power "open" indication light/alarm system |  | 1
Power connection for medicine refrigerator connected to critical power |  | 1
Power connection provided for cabinet security |  | 1
Fixture selected to minimize glare |  | 1
Local switch provided for disconnect of 'hard-wired' equipment. Note for provision of label for each switch |  | 1
Multiple circuits are provided to allow for circuit separation of sensitive equipment |  | 1
Selected equipment and processors provided with critical power circuit |  | 1
Processor equipment connected to UPS where possible, or via isolation transformer |  | 1
Radiology: 'X-Ray In Use' sign above entrance door and interlocked with room lighting control |  | 1
Radiology: nonferrous construction fixtures with no UV, IR, or RF emissions used for MRI suites |  | 1
Conductors to be provided by contractor are clearly identified (size and quantity) |  | 1
Disconnecting means to be provided by contractor is identified |  | 1
Note provided referencing vendor drawings used as basis of design |  | 1
RFI filters provided for MRI rooms |  | 1
Conduits entering Linear Accelerator room at 45 degree or greater relative to iso-center |  | 1
X-ray room lead shield fits behind any flush mounted devices shown in space |  | 1
Isolated ground power is provided for CT Scan equipment if required by vendor |  | 1
Conductors are sized to comply with vendor voltage drop limitations and minimum conductor sizing |  | 1
Fire Alarm Control Panel indicated | [15 empty] | 1
Fire Alarm Voice Evacuation system indicated | [15 empty] | 1
Fire Fighter's Smoke Control Panel indicated | [15 empty] | 1
Area of Rescue assistance, stairwell/elevator lobby communication system base station indicated | [15 empty] | 1
Generator remote annunciator indicated | [15 empty] | 1
Automatic transfer switch control and/or status panel, where provided indicated | [15 empty] | 1
Fire pump remote annunciator, if not integral to fire alarm control panel indicated | [15 empty] | 1
Elevator status remote annunciator indicated | [15 empty] | 1
Security monitors indicated | [15 empty] | 1
Access Control System controls/ stairwell lock overrides indicated | [15 empty] | 1
Master Medical Gas remote alarm panel (two panels) indicated |  | 1
Blood Bank remote alarm indicated |  | 1
Narcotics security alarm indicated |  | 1
Documentation cabinet for fire alarm system documentation indicated | [15 empty] | 1
Method/Space allotted for storage of building design documents | [15 empty] | 1
GFCI devices shown where accessible, or remote protection (breaker or remote trip/reset device) where inaccessible |  |  |  |  | 1
Lighting control allows for safe operation of equipment |  |  |  |  | 1
Shunt trip breakers indicated for food service equipment beneath hood |  |  |  |  | 1
Where required, fixtures are gasketed to prevent grease/insect infiltration |  |  |  |  | 1
In high circuit concentration areas, panelboards are located, flush mounted, within associated space. Provide stainless steel enclosure where required by AHJ. |  |  |  |  | 1
Catwalk configuration allows for proper working clearance for electrical equipment |  |  | 1
Spotlight power connections ((1) L15-30R and (1) 5-20R) are indicated for each spotlight platform |  |  | 1
Photostrobe power connections are indicated (minimum 24-20A/1 circuits for arenas, 30-30A/1 circuits for stadiums. Circuits route through contactor with remote 'off' switch located per owner direction. |  |  | 1
Dimmed or multi-level switched circulation lighting, controlled by lighting control system, is provided at catwalk -part on Emergency circuit |  |  | 1
Acceptance from AHJ received for placement of emergency panelboards on catwalk where seating bowl is not sprinklered |  |  | 1
Company switch or disconnects provided for added power on catwalk for use by owner as needed |  |  | 1
Power provided for house reduction curtain rigging systems |  |  | 1
One GFI receptacle located at each treatment/taping table |  |  | 1
Power indicated for cryotherapy chamber, if required |  |  | 1
Power indicated for bariatric chamber, if required |  |  | 1
Power indicated for ice machines |  |  | 1
Power indicated for Hydrocollator equipment |  |  | 1
Provide minimum 1 duplex for each 2 seats along press seating counter. May require wiremold along counter with pigtail connection to receptacles at the ends of each row. Detail is provided where needed. |  |  | 1
Note is included requiring contractor to provide bonding in accordance with NEC 680 |  |  | 1
Theatrical bars or recessed theatrical fixtures for stage illumination. Separate dimming controller for stage fixtures |  |  | 1
Switches provided for receptacles at dressing counter with indicating light outside space per NEC 520.73 |  |  | 1
Switches provided for lighting at dressing counter, separate from general illumination |  |  | 1
Receptacle is provided in lockable portion of each player locker unit |  |  | 1
Fire alarm control, DACT and NAC panels locations are indicated and life safety/emergency power provided and matches equipment indicated on Fire Alarm riser, if provided | [17 empty] | 1
Consideration of anticipated average ambient sound levels (NFPA 72-A.18.4.4) | [17 empty] | 1
Acoustically distinguishable spaces are noted, special consideration made for intelligibility are denoted (i.e. large lobbies with hard surfaces) | [17 empty] | 1
Notification zones are indicated on floor plans, where other than single zone for the building | [17 empty] | 1
Where multiple notification zones are provided, circuit survivability requirements (NFPA 72-23.10.2, -24.3.13) are indicated and documented for submission to AHJ. (For most projects, level 2 or 3 construction will be required | [17 empty] | 1
Note provided referring to mechanical and fire protection drawings for quantities and locations of duct smoke detectors, flow and tamper switches | [17 empty] | 1
Floor plans are complete | [17 empty] | 1
Proper notification appliance symbols are shown (i.e. speaker vs. horn) | [17 empty] | 1
Smoke detectors are shown in vicinity of any panels containing control functions (NFPA 72-10.4.4). Provide detector whether or not panel is located in an attended location. | [17 empty] | 1
Device layout accounts for sound pressure losses for finishes and through barriers (i.e. 40-45 dBA drop through 4" partition, 12-20 dBA drop through closed hollow core door, 20-30 dBA drop through closed solid core door, 2 dBA drop for acoustic tile ceiling, 3 dBA drop for carpeting) | [17 empty] | 1
Visible notification appliances are not installed in exit stairs (due to increase in trip hazard) | [17 empty] | 1
Visible Devices are shown in required public mode spaces: restrooms, conference rooms, training rooms, waiting rooms, lobbies, lounges, etc. | [17 empty] | 1
Where mechanical design includes engineered smoke control zones, the sprinkler zoning and fire alarm zoning matches the smoke zoning | [17 empty] | 1
Visible notification appliances are placed within 15' of the end of corridors | [17 empty] | 1
Where required by code, smoke detectors are provided within 10' of the entrance to stair tower at each level for activation of stairwell smoke pressurization system. | [17 empty] | 1
Manual pull stations are located within 5' from exit doorways at each level, and on both sides of grouped openings over 40' wide. Intermediate pull stations located for travel distances over 200'. (NFPA 72-17.14.8., 101-9.6.2, IBC 907.6) | [17 empty] | 1
At least one pull station is provided near FACP for facilities for which manual pull stations are omitted and only automatic initiation means are provided (i.e. arenas) (NFPA 101-9.6.2.6) | [17 empty] | 1
Smoke detectors are located more than 26" horizontal path from door to a bathroom containing a shower or tub (unless detector is listed for the application) (NFPA 101-9.6.2.10.5, IBC 907.2.11.4) | [17 empty] | 1
Smoke detectors are not located within 10' of fixed cooking equipment (unless listed for installation). Detectors installed between 10' and 20' from fixed cooking equipment shall have alarm silencing means or be photoelectric type.(NFPA 101-9.6.2.10.4, IBC 907.2.11.3) | [17 empty] | 1
Voice system is specified for High rise, assembly occupancies over 1000 occupants, educational, and mercantile occupancies) (IBC 907.2) | [17 empty] | 1
First responder radio system/DAS is connected to Life Safety/Emergency power and generator and/or battery system allows for an operating duration of not less than 24 hours. (IBC 2702.2.3) | [17 empty] | 1
Approval received from AHJ if Pre-Signal Alarm sequence is specified (NFPA 101, NFPA 72-23.8.1) | [17 empty] | 1
Approval received from AHJ if Positive Alarm sequence is specified (NFPA 101, NFPA 72-23.8.1) | [17 empty] | 1
Detectors required for elevator recall and shutdown are shown in lobbies, shaft and equipment room | [17 empty] | 1
Low frequency sounder base detectors and high candela strobes are shown in public mode notification area sleeping rooms/on-call rooms | [17 empty] | 1
Anticipated control panels, NAC panels and remote annunciators are indicated | [17 empty] | 1
Wiring configuration (Class A vs. Class B) corresponds to specifications | [17 empty] | 1
Areas where circuit survivability are required are indicated with the survivability level | [17 empty] | 1
Return path for Class A communications loop is identified, where applicable | [17 empty] | 1
Sequence of operation is included and edited for project specific requirements | [17 empty] | 1
Provisions are included in base bid for Bi-Directional Antenna system riser cable routing, roof access, control panel and annunciator panel mounting. Specifications include complete system installation as a bid alternate (for owner purchase if coverage is determined to be needed based on as built audio survey once structure and skin are constructed). | [16 empty] | 1
2-HR room and riser pathway for system are included in documents | [16 empty] | 1
Power circuit provided | [16 empty] | 1
Proposed annunciator location is indicated | [16 empty] | 1
System schematic is provided | [16 empty] | 1

## Revision Log (hidden)
Revision Date | Description of Change
2025-10-20 | Added Excel version with updated content